## Slide 1
Rigger Checkpoints while preparing Model Sites
S.No. | Checkpoint
1 | Weatherproofing of each GSM antenna in 03 Parts (1st wrap of Tape from Bottom to Top, 2nd Wrap of Weatherproofing from bottom to top from 2-3 cm below of 1st wrap, 3rd Wrap of Tape from bottom to top from 2-3 cm below of 2nd wrap)
2 | Put Tie on bottom & Top of weatherproofing to ensure its long life
3 | Check the condition & proper fixing of rubber boots (in case rubber boots installed on Jumpers)
4 | In case Rubber boot is not proper, Weatherproofing to be done properly after removing rubber boot & then put the boot again on connector.
5 | RF Antenna Height, Orientation, Tilt (Electrical & Mechanical) are as per GIS in each sector for all Antenna's.
6 | Tightning of Clamp nut bolts of RF Antenna
7 | Check the tightning of Pole mount as well
8 | Check the condition of Tilt (Free from damage & working)
9 | Weatherproofing of each MW Antenna in 03 Parts (1st wrap of Tape from Bottom to Top, 2nd Wrap of Weatherproofing from bottom to top from 2-3 cm below of 1st wrap, 3rd Wrap of Tape from bottom to top from 2-3 cm below of 2nd wrap)
10 | Tightening of Clamp nut bolts of MW Antenna
11 | Check the tightening of MW Pole mount as well
12 | Check earthing of ODU (Presence & tightning)
13 | Labeling & Marking on MW Antenna (Orientation, Far end detail)
14 | Check the direction of ODU connector (Should be towards Ground) to avoid water seepage
15 | Check the installation of support Rod as per standard practice & photo. Also, check the tightening of all nut & bolts. 01 support required for .9m Antenna & 2 support required for 1.2/1.8m MW Antenna
16 | Check the IF Cable loop availability & its proper routing. Also check LAN & Power cable loop in case of IP20C ODU
17 | Paint Marks at connecting point of Pole Mount & Antenna Clamp (Helpful during Link misaligned)
18 | Availability of Lightning Arrestor (If not, mention the point in Infra Hygiene)
19 | Cable routing from Top to bottom of tower (No sagging, mess of cables & loose cables on Tower)
20 | In case of OD BTS Weatherproofing of each Jumper Feeder connection in 03 Parts (1st wrap of Tape from Bottom to Top, 2nd Wrap of Weatherproofing from bottom to top from 2-3 cm below of 1st wrap, 3rd Wrap of Tape from bottom to top from 2-3 cm below of 2nd wrap)
21 | Earthing of Feeders near Horizontal OD ladder to be done & sealed properly.
22 | Note all unused RF & MW Antennas along with size
23 | DC junction box should be sealed properly & free from any type of water seepage
24 | All free ports of RF module should be filled with IP seals/proper seal.
25 | Check any blocking in front of RF/MW Antenna
26 | GPS antenna & Connector tightening & positioning of GPS Antenna
27 | GPS cable routing & is free from cut & damage
Hard copy to be given in Regional language to all riggers